## Index
DRASTIC
Power System Calculator
This calculator is designed to assist our customers in determining the electrical power
system that they need for their application.
The power system is designed to provide clean, stable, uninterrupted power to key
equipment. Protecting ALL of your electrical equipment could be expensive and
probably unnecessary. We recommend that you size your power system for the
protection of key equipment only.
Key: | = cell where you can enter your data
= cell containing calculated data: do not change.
There are a three of steps to go through:
1. Calculate the AC power load for the equipment that you want to power.
2. Calculate the required battery size
3. Verify recharging performance
© Copyright DRASTIC LLC, 2006
www.drasticom.org | info@drasticom.org | Tel: +1 704-644-8382

## Calculate Load
DRASTIC
Power System Calculator |  |  |  |  | Back to Index
Step 1: Calculate the AC power load
List below the equipment that you want to protect together with their AC Load
in Watts (Watts = Volts x Amps)
Starting data is sample only. Insert your own data. Check the power consumption
of your actual equipment: don't just accept the sample data.
|  | Number | Maximum
Description of Devices | Watts | of devices | Load
VSAT Modem with 5W BUC | 130 | 1 | 130
Router / Bandwidth manager (dedicated device) | 50 | 1 | 50
WLAN Access Point | 25 | 1 | 25
LAN Switch | 25 | 1 | 25
VPN Appliance | 50 | 1 | 50
Desktop computers | 400 | 2 | 800
Servers | 400 | 1 | 400
Laptop computers | 80 | 0 | 0
Printers | 100 | 1 | 100
CRT screens | 150 | 0 | 0
LCD screens | 50 | 2 | 100
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
| 0 | 0 | 0
Typical Maximum Load |  |  | 1680 | Watts
Notes
Inverter efficiency |  |  | 92% |  | Outback inverters are typically 92% efficient.
Minimum Inverter capacity at calculated load |  |  | 1826.087 | Watts | Outback inverter/chargers are available in several sizes
in both vented and sealed models.
Preferred inverter system DC voltage |  |  | 24 | VDC
Sealed: 2000W @ 12VDC or 24VDC; 2300W @48VDC
Current drain from battery at maximum load |  |  | 76.087 | Amps | Vented: 2600W@12VDC; 3000W @ 24VDC or 48VDC
Higher capacities are achieved by stacking multiple units.
Back to Index
© Copyright DRASTIC LLC, 2006

## Calculate Battery Size
DRASTIC
Power System Calculator |  |  | Back to Index
Step 2: Calculate required battery size
From Step 1, we have established:
Typical maximum load will be | 1826.087 | Watts | Notes
Current drain from battery at maximum load will be | 76.087 | Amps
Inverter system voltage | 24 | Volts
How many hour maximum power outage are you budgeting for? | 6 | Hours
Normal storage capacity in Amp hours | 456.5217 | A/h | = current drain(Amps) x outage period(hours)
Maximum drawdown | 50% |  | Repeated overdischarging will severely shorten battery life.
It is recommended not to discharge beyond 50% of battery capacity
Inverter can be set to automatically switch off at this level
to prevent battery damage.
Required battery capacity in Amp Hours | 913.0435 | A/h
Derating factor for cold weather | 100% |  | Batteries do not perform as well in cold weather
If you store the batteries in cold conditions, a derating factor
Total required rated battery capacity in Amp Hours | 913.0435 | A/h | should be used.
How many batteries do you need and how should the be
configured?
What is the voltage of a single battery? | 6 | Volts | Normally 6, 12 or 24 volts
Single battery capacity in Amp Hours | 225 | A/h | Take this from the battery manufacturer data.
Number of batteries in Series for required voltage | 4 |  | = System voltage / individual battery voltage
Number of batteries banks in Parallel (for required capcity) | 4 |  | = total required battery capacity/available capacity per battery
Total number of specified batteries required | 16
Back to Index
© Copyright DRASTIC LLC, 2006

## Verify recharging
DRASTIC
Power System Calculator |  |  | Back to Index
Step 3: Verify re-charging performance
These calculations check that the inverter/charger can handle
the necessary charging capacity and that it can recharge the
batteries within the available charging time.
Notes
First, check the charger rating (Amps)
Available recharging time in hours | 12 | Hours | How long will the power be ON? (Generator / Grid power)
Charging efficiency | 95% |  | This accounts for the inefficiencies in wiring and batteries
Maximum battery capacity to be replenished | 456.5217 | A/h | (based on Normal storage capacity in Amp hours from Step 2.)
Charger current capacity | 36 | Amps | Maximum charger capacities for Outback inverters are:
Sealed: 12VDC @ 100A, 24VDC @55A, 48VDC @35A
Second, check time required to re-charge (hrs) |  |  | Vented: 12VDC @ 120A, 24VDC @85A, 48VDC @42A
Inverter charger maximum charging capacity | 85 | Amps | See notes above to select an inverter with adequate capacity
Charging efficiency | 95% |  | This accounts for the inefficiencies in wiring and batteries
Maximum battery capacity to be replenished | 456.5217 | A/h | (based on Normal storage capacity in Amp hours from Step 2.)
Recharging time at maximum charge rate | 5.6535 | Hours | Check that this is possible with the Generator/grid power available!
Back to Index
© Copyright DRASTIC LLC, 2006